## CombinedLevelsExternal
MasterMark | Location | Type | Level | Type Description | Width | Height | Min Clear Width | SpecRef | Fire Rating | Acoustic Rating | Access Control | Operation/Security | Access Control | Gas Suppression Requirements | Comments | Ironmongery Set | Door Frame Colour | Door Leaf/Transom/Overpanel Colour
ED-10-001 | Courtyard 04 | EDT 8a | Level 0 | Hinged, aluminium-framed glazed, double door in curtain walling | 1850 | 2410 |  | H11/136A | N/A | N/A | No |  | No |  | Door located in curtain walling. | E5d | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-002 | Pathology Access | EDT 3b OP | Level 0 | Hinged, steel, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | N/A | N/A | Yes | Door contacts | Yes |  |  | E3c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-003 | FM in | EDT 5a | Level 0 | Overhead sectional door with passdoor | 5750 | 3135 |  | L20/616 | N/A | N/A | No | Door contact/ powered | No |  |  | as L20/616 | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-004 | FM WC | EDT 1b OP | Level 0 | Hinged, steel, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No |  | Yes |  |  | E2 | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-005 | FM WC | EDT 1b OP | Level 0 | Hinged, steel, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No |  | Yes |  |  | E2 | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-006 | FM out | EDT 3b OP | Level 0 | Hinged, steel, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | N/A | N/A | Yes | Door contacts | Yes |  |  | E3c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-007 | Pharmacy | EDT 5a | Level 0 | Overhead sectional door with passdoor | 3000 | 3135 |  | L20/616 | N/A | N/A | No | Door contact/ powered | No |  |  | as L20/616 | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-008 | Pharmacy | EDT 3b OP | Level 0 | Hinged, steel, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | N/A | N/A | Yes | Door contacts | Yes |  |  | E3c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-009 | Mortuary | EDT 3b OP | Level 0 | Hinged, steel, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | N/A | N/A | Yes | Door contacts | Yes |  |  | E3c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-010 | Courtyard 01 | EDT 8a | Level 0 | Hinged, aluminium-framed glazed, double door in curtain walling | 1850 | 2495 |  | H11/136A | N/A | N/A | No |  | No |  | Door located in curtain walling. | E5d | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-011 | Courtyard 03 | EDT 8a | Level 0 | Hinged, aluminium-framed glazed, double door in curtain walling | 1850 | 2495 |  | H11/136A | N/A | N/A | No |  | No |  | Door located in curtain walling. | E5d | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-012 | Courtyard 03 | EDT 8a | Level 0 | Hinged, aluminium-framed glazed, double door in curtain walling | 1850 | 2495 |  | H11/136A | N/A | N/A | No |  | No |  | Door located in curtain walling. | E5d | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-101 | ED walk-in entrance | EDT 4a | Level 1 | Automatic, bi-folding, aluminium-framed glazed, fold in | 2150 | 2535 | 1500 | H11/134A | N/A | N/A | Yes | Powered | No |  | Visual contrast achieved with manifestation | as H11/134A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-102 | ED ambulance entrance | EDT 4a | Level 1 | Automatic, bi-folding, aluminium-framed glazed, fold in | 2450 | 2535 | 1900 | H11/134A | N/A | N/A | Yes | Powered | No |  | Visual contrast achieved with manifestation | as H11/134A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-103 | Decontamination / AMB wash | EDT 1b OP | Level 1 | Hinged, steel, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | Yes |  | Yes |  |  | E3b | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-104 | Decontamination / AMB wash | EDT 1b OP | Level 1 | Hinged, steel, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | Yes |  | Yes |  |  | E3b | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-201 | Access to level 2 Z30 roof | EDT 14a | Level 2 | Hinged, aluminium-framed, glazed, single doorset | 1060 | 2110 |  | L20/ 487 | N/A | N/A | No |  | No |  | Emergency roof exit | E5c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-202 | FM circulation to CAU roof | EDT 7a | Level 2 | Hinged, aluminium-framed glazed, single door in curtain walling | 1060 | 1940 |  | H11/136A | N/A | N/A | No |  | No |  | Emergency roof exit | E5c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-301 | Wait/ Play | EDT 14a | Level 3 | Hinged, aluminium-framed, glazed, single doorset | 1060 | 1800 |  | L20/ 487 | N/A | N/A | No |  | No |  | Emergency roof exit | E5c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-302 | Staff rest | EDT 14a | Level 3 | Hinged, aluminium-framed, glazed, single doorset | 1060 | 1800 |  | L20/ 487 | N/A | N/A | No |  | No |  | Emergency roof exit | E5c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-10-501 | Stair 1 to roof | EDT 3b | Level 5 | Hinged, steel, double doorset | 1810 | 2110 |  | L20/481 | N/A | N/A | No |  | No |  | Emergency roof exit | E5b | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-10-502 | Core A LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 1210 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-503 | Core B LMR to roof | EDT 2b | Level 5 | Hinged, steel, leaf and a half doorset | 1710 | 2410 |  | L20/481 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-504 | Core E LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 1210 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-506 | Core F LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 1210 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-507 | Core G LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 1210 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-508 | Core A LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 750 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-509 | Core E LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 750 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-510 | Core F LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 750 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-10-511 | Core G LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 1210 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-001 | Stair 03 final exit | EDT 2b OP | Level 0 | Hinged, steel, leaf and a half doorset, with overpanel | 1710 | 2535 | 1500 | L20/481 | N/A | N/A | No | Monitored contact 24hr. | No |  | Emergency push bars. | E4c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-20-002 | Courtyard 01 | EDT 3b OP | Level 0 | Hinged, steel, double doorset, with overpanel | 1900 | 2535 |  | L20/481 | N/A | N/A | No |  | No |  |  | E1c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-20-003 | CAU plantroom | EDT 3e | Level 0 | Hinged, louvre screening, double | 2510 | 2560 |  | L10/652 | N/A | N/A | No | Monitored contact 24hr. Deadlock with external suited cylinder / internal thumbturn. | No |  | Door is located within louvre system. | E1c |  | Anthracite Grey (RAL 7016)
ED-20-004 | Courtyard 02 | EDT 8a | Level 0 | Hinged, aluminium-framed glazed, double door in curtain walling | 1900 | 2060 |  | H11/136A | N/A | N/A | No |  | No |  | Door located within curtain walling. | E5d | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-20-101 | CAU ambulance entrance | EDT 4a | Level 1 | Automatic, bi-folding, aluminium-framed glazed, fold in | 2450 | 2535 | 1500 | H11/134A | N/A | N/A | Yes | External / internal PIR sensors. Fail safe on alarm. Daytime - open access. Nighttime - access control reader 'in' / request to exit. | Powered |  | Internal guarding required. In curtain walling. Visual contrast achieved with manifestation | as H11/ 134A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-20-102 | MRI Access | EDT 17b | Level 1 | Hinged, steel, double doorset | 3310 | 3135 | 3000h x 3000w | L20/ 488 | N/A | N/A | No |  | No |  |  | E8 | Sirius Matt (RAL 9006) | Sirius Matt (RAL 9006)
ED-20-103 | CAU walk-in entrance | EDT 4a | Level 1 | Automatic, bi-folding, aluminium-framed glazed, fold in | 2450 | 2535 | 1500 | H11/134A | N/A | N/A | No | External / internal PIR sensors. Fail safe on alarm. | Powered |  | Internal guarding required. In curtain walling. Visual contrast achieved with manifestation | as H11/ 134A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-20-201 | IPU to CAU roof | EDT 7a | Level 2 | Hinged, aluminium framed glazed, single door in curtain walling | 1125 | 2060 |  | H11/136A | N/A | N/A | No |  | No |  |  | E5c | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-20-501 | IPU Plant room to roof (east) | EDT 3b OP | Level 5 | Hinged, steel, double doorset, with overpanel | 1810 | 2420 |  | L20/481 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-502 | IPU Plant room to roof (east) | EDT 3b OP | Level 5 | Hinged, steel, double doorset, with overpanel | 1810 | 2420 |  | L20/481 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-503 | Core C LMR to roof | EDT 1c TP | Level 5 | Hinged, steel-framed louvred, single doorset | 1210 | 2110 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-504 | IPU Plant room to roof (east) | EDT 3b OP | Level 5 | Hinged, steel, double doorset, with overpanel | 1810 | 2420 |  | L20/481 | N/A | N/A | No |  | No |  |  | E1c | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-505 | Stair 3 to roof | EDT 1b OP | Level 5 | Hinged, steel, single doorset, with overpanel | 1060 | 2590 |  | L20/481 | N/A | N/A | No |  | No |  |  | E5a | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-506 | IPU Plant room to roof (west) | EDT 1b OP | Level 5 | Hinged, steel, single doorset, with overpanel | 1060 | 2420 |  | L20/481 | N/A | N/A | No |  | No |  |  | E5a | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-507 | IPU Plant room to roof (west) | EDT 1b OP | Level 5 | Hinged, steel, single doorset, with overpanel | 1060 | 2420 |  | L20/481 | N/A | N/A | No |  | No |  |  | E5a | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-20-508 | IPU Plant room to roof (west) | EDT 1b OP | Level 5 | Hinged, steel, single doorset, with overpanel | 1060 | 2420 |  | L20/481 | N/A | N/A | No |  | No |  |  | E5a | Light Grey (RAL 7035) | Light Grey (RAL 7035)
ED-30-001 | SFM locker area | EDT 1b | Level 0 | Hinged, steel, single doorset | 1060 | 2110 |  | L20/481 | N/A | N/A | Yes | Access control reader 'in' / request to exit. | Delayed action self closing |  | External pull handle. 90° restrictor. | E3a | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-002 | SFM locker area | EDT 1b | Level 0 | Hinged, steel, single doorset | 1060 | 2110 |  | L20/481 | N/A | N/A | No | Emergency push bar. | No |  | Monitored contact 24hr. 90° restrictor. | E4a | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-003 | SFM locker area | EDT 1b OP | Level 0 | Hinged, steel, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No | Emergency push bar. | No |  | Monitored contact 24hr. 90° restrictor. | E4a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-30-004 | PTS Access | EDT 4a | Level 0 | Automatic, bi-folding, aluminium-framed glazed, fold in | 2150 | 2535 |  | H11/134A | N/A | N/A | Yes | External / internal PIR sensors. Fail safe on alarm. Access control reader 'in' / request to exit. | Powered |  | Visual contrast achieved with manifestation. | as H11/134A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-005 | Pathology exit (east) | EDT 1a OP | Level 0 | Hinged, steel, glazed, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No | Emergency push bar. | No |  | Monitored contact 24hr. 90° restrictor. | E4a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-30-006 | ENT Office | EDT 1b OP | Level 0 | Hinged, steel, single doorset, with overpanel | 1060 | 2440 |  | L20/481 | N/A | N/A | No | Deadlock with internal / external suited cylinder. | No |  | Monitored contact 24hr. 90° restrictor. | E1b | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-007 | Main entrance - outer | EDT 9a | Level 0 | Powered, telescopic sliding doors, aluminium-framed glazed, in curtain walling | 3560 | 2290 |  | L20/491 | N/A | N/A | No | External / internal PIR sensors. Fail safe on alarm | Powered |  | Visual contrast achieved with manifestation. | as H11/135A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-008 | Main entrance - inner | EDT 4a | Level 0 | Automatic, bi-folding, aluminium-framed glazed, fold in | 2730 | 2600 |  | H11/134A | N/A | N/A | Yes | External / internal PIR sensors. Fail safe on alarm. Daytime - open access. Nighttime - access control intercom and reader 'in' / request to exit. | Powered |  | Monitored contact. In curtain walling. | as H11/134A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-009 | Pass door thru external GRC/concrete screen | EDT 18b | Level 0 | Hinged, steel, single doorset | 1060 | 2110 |  | L20/489 | N/A | N/A | No | Openable from courtyard side only. | No |  | Door to be clad with GRC panels as spec ref: H92/119A. Refer to detail drawing P012X-BDP-A- DT-XX-X-31106 | E7 | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-010 | Discharge | EDT 18a | Level 0 | Powered, bi-parting sliding doors, aluminium-framed glazed, in curtain walling | 1800 | 2512 |  | H11/138A | N/A | N/A | No | External / internal PIR sensors. Fail safe on alarm | Powered |  | Visual contrast achieved with manifestation. | as H11/138A | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-101 | Restaurant to terrace roof | EDT 6a | Level 1 | Folding / sliding, aluminium-framed glazed, in curtain walling | 5150 | 2495 |  | L20/491 | N/A | N/A | No | Secure multi-point lock | No |  |  | as L20/491 | Basalt Grey (RAL 7012) | Basalt Grey (RAL 7012)
ED-30-103 | External stair 1 | EDT 1b | Level 1 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | Emergency push bar. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-104 | External stair 2 | EDT 1b | Level 1 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | Emergency push bar. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-201 | External stair 1 | EDT 1b | Level 2 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | Emergency push bar. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-202 | External stair 2 | EDT 1b | Level 2 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | Emergency push bar. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-301 | External stair 1 | EDT 1b | Level 3 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | Emergency push bar. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-302 | External stair 2 | EDT 1b | Level 3 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | Emergency push bar. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-401 | External stair 1 | EDT 1b | Level 4 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-402 | External stair 2 | EDT 1b | Level 4 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD60S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-403 | External stair 2 | EDT 1b | Level 4 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-427 | External stair 1 | EDT 1b | Level 4 | Hinged, steel, single doorset | 900 | 2110 |  | L20/481 | FD60S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-428 | External stair 1 | EDT 1b | Level 4 | Hinged, steel, single doorset | 900 | 2110 |  | L20/481 | FD60S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-501 | Plant | EDT 3e | Level 5 | Hinged, louvre screening, double | 2010 | 2200 |  | L10/651 | N/A | N/A | No | Deadlock with internal / external suited cylinder. | No |  | Door is located within louvre | E1e |  | Basalt Grey (RAL 7012)
ED-30-502 | Plant room to external stair 1 | EDT 1b | Level 5 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-30-503 | Plant | EDT 3e | Level 5 | Hinged, louvre screening, double | 2010 | 2200 |  | L10/651 | N/A | N/A | No | Deadlock with internal / external suited cylinder. | No |  | Door is located within louvre | E1e |  | Basalt Grey (RAL 7012)
ED-30-504 | External stair 2 | EDT 1b | Level 5 | Hinged, steel, single doorset | 1310 | 2110 |  | L20/481 | FD30S | N/A | No | External suited cylinder / internal thumbturn. | Yes |  | Monitored contact 24hr. FDKL signs. 90° restrictor. | E4b | White Aluminium (RAL 9006) | White Aluminium (RAL 9006)
ED-40-001 | LV switch & UPS | EDT 1b OP | Level 0 | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No | TBC |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-002 | LV switch & UPS | EDT 3b OP | Level 0 | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No | TBC |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-003 | LV switch & UPS | EDT 1b OP | Level 0 | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No | TBC |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-004 | LV switch & UPS | EDT 1b OP | Level 0 | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No | TBC |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-005 | LV switch & UPS | EDT 3b OP | Level 0 | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | FD60S | N/A | No | Monitored contact 24hr | No | TBC |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-006 | Pathology Gas Compound | EDT 3e | Level 0 | Hinged, louvre screening, double | 2000 | 2135 |  | Q40A/436 | N/A | N/A | No |  | No |  | Door is located within louvre | E1e |  | Anthracite Grey (RAL 7016)
ED-40-007 | Flammable store | EDT 1c OP | Level 0 | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2535 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-008 | Bottle store | EDT 3c OP | Level 0 | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2535 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-009 | Dry linen hold | EDT 3c OP | Level 0 | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2535 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-010 | EC White Space | EDT 3b OP | Level 0 - EC | Hinged, steel, double doorset, with overpanel | 1810 | 2565 |  | L20/481 | N/A | N/A | No | Door contacts 24hr/alarm | No |  |  | E1c | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-011 | EC Corridor West | EDT 1d OP | Level 0 - EC | Hinged, steel-framed, single doorset, with louvred overpanel | 1060 | 2565 |  | L20/481 | N/A | N/A | No | Door contact 24hr/alarm | No |  |  | E1a | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-012 | EC White Space | EDT 3b OP | Level 0 - EC | Hinged, steel, double doorset, with overpanel | 1810 | 2565 |  | L20/481 | N/A | N/A | No | Door contacts 24hr/alarm | No |  |  | E1c | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-013 | EC Engineers Workshop | EDT 3b OP | Level 0 - EC | Hinged, steel, double doorset, with overpanel | 1810 | 2565 |  | L20/481 | N/A | N/A | No | Door contacts 24hr/alarm | No |  |  | E1c | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-014 | EC Corridor North | EDT 1b OP | Level 0 - EC | Hinged, steel, single doorset, with overpanel | 1060 | 2565 |  | L20/481 | N/A | N/A | Yes | Door contact 24hr/alarm | Yes |  |  | E3a | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-015 | EC Builders workshop | EDT 3b | Level 0 - EC | Hinged, steel, double doorset | 2410 | 2560 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No |  |  | E1f | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-019 | Bin store | EDT 3e | Level 0 - EC | Hinged, louvre screening, double | 2000 | 2110 |  | Q40A/436 | N/A | N/A | No |  | No |  | Door is located within louvre | E1e |  | Anthracite Grey (RAL 7016)
ED-40-020 | Bin store | EDT 3e | Level 0 - EC | Hinged, louvre screening, double | 2000 | 2110 |  | Q40A/436 | N/A | N/A | No |  | No |  | Door is located within louvre | E1e |  | Anthracite Grey (RAL 7016)
ED-40-021 | Bin store | EDT 3e | Level 0 - EC | Hinged, louvre screening, double | 2000 | 2110 |  | Q40A/436 | N/A | N/A | No |  | No |  | Door is located within louvre | E1e |  | Anthracite Grey (RAL 7016)
ED-40-022 | Bin store | EDT 1e | Level 0 - EC | Hinged, louvre screening, single | 1000 | 2110 |  | Q40A/436 | N/A | N/A | No |  | No |  | Door is located within louvre | E1d |  | Anthracite Grey (RAL 7016)
ED-40-023 | Bin store | EDT 1e | Level 0 - EC | Hinged, louvre screening, single | 1000 | 2110 |  | Q40A/436 | N/A | N/A | No |  | No |  | Door is located within louvre | E1d |  | Anthracite Grey (RAL 7016)
ED-40-024 | LV switch & UPS | EDT 3b OP | Level 0 | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2535 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No | TBC |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-025 | LV switch & UPS | EDT 1b OP | Level 0 | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2535 |  | L20/481 | N/A | N/A | No | Monitored contact 24hr | No | TBC |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B01 | EC Oxygen Store | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B02 | EC Plant | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B03 | EC Nitrous Oxide Store | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B04 | EC Plant | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B05 | EC Plant | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B06 | EC Plant | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B07 | EC Plant | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B08 | EC Water tanks | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B09 | EC LV A | EDT 3c | Level B - EC | Hinged, steel-framed louvred, double doorset | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1f | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B10 | EC LV B | EDT 3c | Level B - EC | Hinged, steel-framed louvred, double doorset | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1f | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B11 | EC Boiler Room | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 2410 | 3405 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B12 | EC Boiler Room | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 2410 | 3405 |  | L20/482 | N/A | N/A | No |  | No |  | Door abuts louvre panel | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B13 | EC Pumps | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B14 | EC EDC | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2805 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B19 | Switch rooms - HV2 | EDT 16a | Level B - EC | Demountable double doorset & side panels. S/O as scheduled. Refer to elevation for further information | 4000 | 2600 |  | L20/486 | N/A | N/A | No |  | No |  | Demountable double doorset & side panels. S/O as scheduled. Refer to elevation for further information | E6b | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-B20 | Switch rooms - HV1 | EDT 16a | Level B - EC | Demountable double doorset & side panels. S/O as scheduled. Refer to elevation for further information | 4000 | 2600 |  | L20/486 | N/A | N/A | No |  | No |  | Demountable double doorset & side panels. S/O as scheduled. Refer to elevation for further information | E6b | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-B22 | Switch rooms - HV2 | EDT 1b OP | Level B - EC | Hinged, steel, single doorset, with overpanel | 1060 | 2600 |  | L20/481 | N/A | N/A | No |  | No |  |  | E6a | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-B24 | Switch rooms - HV1 | EDT 1b OP | Level B - EC | Hinged, steel, single doorset, with overpanel | 1060 | 2600 |  | L20/481 | N/A | N/A | No |  | No |  |  | E6a | Telegrey 4 (RAL 7047) | Anthracite Grey (RAL 7016)
ED-40-B25 | Switch rooms - LVB | EDT 1c OP | Level B - EC | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2670 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B26 | Switch rooms - LVB | EDT 1c OP | Level B - EC | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2570 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B27 | Switch rooms - Trans 2 | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 2510 | 2570 | 2400 | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B28 | Switch rooms - LVB | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2570 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B29 | Switch rooms - LVB | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 1810 | 2670 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B30 | Switch rooms - Trans 1 | EDT 3c OP | Level B - EC | Hinged, steel-framed louvred, double doorset, with overpanel | 2510 | 3020 | 2400 | L20/482 | N/A | N/A | No |  | No |  |  | E1c | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B31 | Switch rooms - Trans 1 | EDT 1c OP | Level B - EC | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 3020 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)
ED-40-B32 | Switch rooms - Trans 2 | EDT 1c OP | Level B - EC | Hinged, steel-framed louvred, single doorset, with overpanel | 1060 | 2570 |  | L20/482 | N/A | N/A | No |  | No |  |  | E1a | Anthracite Grey (RAL 7016) | Anthracite Grey (RAL 7016)

## SetRefsExternal
Set ref | DoorType | Leaf | Swing | Fire | Xray | PowerCloserDelay | PullOrLever | Lock | SlaveLeafBolted | AccessControl | Direction | KickPlate | Mid-rail | FingerProtection | TypicalUses | SetDetails
E1a | Steel | 1 | Single | - |  | Restrictor | Lever | Cylinder/thumbturn | N/A | - | N/A | - | - | - | External stores, Energy Centre | 1.5pr. hinges; sashlock, master-keyed security cylinder and turn, 1pr. Euro escutcheons, 1pr. lever handles on roses; 90° hold-open restrictor; 50mm dia. Door ID disc
E1b | Steel | 1 | Single | - |  | Closer | Lever | Cylinder/thumbturn | N/A | - | N/A | - | - | - | Office | 1.5pr. hinges; sashlock, master-keyed security cylinder and turn, 1pr. Euro escutcheons, 1pr. lever handles on roses; adjustable power overhead closer with backcheck; 50mm dia. Door ID disc
E1c | Steel | 1.5 / 2 | Single | - |  | 2 Restrictors | Lever | Cylinder/thumbturn | Flush | - | N/A | - | - | - | Lift motor room, external stores, Energy Centre (assumed for level B - no security layout) | 3pr. hinges; sashlock, master-keyed security cylinder and turn, 1pr. Euro escutcheons, 1pr. lever handles on roses; 2no. flush bolts; 2no. 90° hold-open restrictors; 50mm dia. Door ID disc
E1d | Louvred | 1 | Single | - |  | Restrictor | Lever | Cylinder/thumbturn | N/A | - | N/A | - | - | - | Bin Store | 1pr. FAC adjustable hinges; lock, master-keyed security cylinder and turn, 1pr. lever handles on roses; 90° hold-open restrictor; 50mm dia. Door ID disc
E1e | Louvred | 2 | Single | - |  | 2 Restrictors | Lever | Cylinder/thumbturn | Surface | - | N/A | - | - | - | Pathology Gas Compound, Bin Store | 2pr. FAC adjustable hinges; lock, master-keyed security cylinder and turn, 1pr. lever handles on roses; 2no. Anti-lift drop bolts; 2no. 90° hold-open restrictors; 50mm dia. Door ID disc
E1f | Steel | 2 | Single | - |  | 2 Restrictors | Lever | 2no. Cylinder/ thumbturn | Surface | - | N/A | - | - | - | Builders Workshop, LV rooms (over-height leaves) | 5pr. hinges; 1no. sashlock, 1no. master-keyed security cylinder and turn, 1pr. Euro escutcheons, 1pr. lever handles on roses; 1no. deadlock, 1no. master-keyed security cylinder and turn, 1pr. Euro escutcheons; 450mm surface bow handle bolt (bottom); 900mm surface bow handle bolt (top); 2no. 90° hold-open restrictors (extra heavy duty); 50mm dia. Door ID disc
E2 | Steel | 1 | Single | - |  | Closer | Lever | Bathroom lock + Lock | N/A | - | N/A | - | - | - | FM wc | 1.5pr hinges; bathroom lock, bathroom indicator on rose, extended bathroom turn on rose, 1pr lever handles on roses; deadlock, master-keyed security single cylinder (external only), Euro escutcheon; adjustable power overhead closer with backcheck; 50mm dia. Door ID disc
E3a | Steel | 1 | Single | - |  | Closer | Pull | - | N/A | Maglock | Out | - | - | - | Staff change entrance, Energy Centre entrance | 1.5pr. Hinges; adjustable power overhead closer with backcheck; 450mm bolt through pull handle, 500 x 75mm push plate; monitored electro magnetic lock; 50mm dia. Door ID disc
E3b | Steel | 1 | Single | - |  | Delay | Pull | - | N/A | Maglock | Out | - | - | - | Decontamination | 1.5pr. Hinges; adjustable power overhead closer with delay action and backcheck; 450mm bolt through pull handle, 500 x 75mm push plate; monitored electro magnetic lock; 50mm dia. Door ID disc
E3c | Steel | 2 | Single | - |  | 2 Delay | Pull | - | - | Double Maglock | Out | - | - | - | Pathology access, FM out | 3pr. Hinges; 2no. adjustable power overhead closers with delay action and backcheck; 2no. 450mm bolt through pull handles, 2no. 500 x 75mm push plates; double monitored electro magnetic lock; 50mm dia. Door ID disc
E4a | Steel | 1 | Single | - |  | Restrictor | - | - | N/A | - | N/A | - | - | - | Pathology, Staff change | 1.5pr. Hinges; single touch bar panic exit device; 90° hold-open restrictor; 50mm dia. Door ID disc
E4b | Steel | 1 | Single | FD30S |  | Closer | - | External cylinder | N/A | - | N/A | - | - | - | Restaurant, Office emergency exit, Plant Room | 1.5pr. Hinges; single touch bar panic exit device with external lock, single master-keyed security cylinder, Euro escutcheon; adjustable power overhead closer with backcheck; 2no. 76mm dia. Bi-lingual Fire Door Keep Shut signs; 50mm dia. Door ID disc
E4c | Steel | 1.5 | Single | - |  | 2 Restrictors | - | External cylinder | - | - | N/A | - | - | - | Final exit | 3pr. Hinges; double touch bar panic exit device with external lock, single master-keyed security cylinder, Euro escutcheon; 2no. 90° hold-open restrictors; 50mm dia. Door ID disc
E5a | Steel | 1 | Single | - |  | Restrictor | Single lever | Cylinder inside only | N/A | - | N/A | - | - | - | Stair / plant rooms with emergency egress from roof | 1.5pr. hinges; sashlock, single master-keyed security cylinder and turn, 1no. Euro escutcheon, 1no. lever handle on rose; 90° hold-open restrictor; 50mm dia. Door ID disc (external lever handle to release lock bolt for emergency egress)
E5b | Steel | 2 | Single | - |  | 2 Restrictors | Single lever | Cylinder inside only | Flush | - | N/A | - | - | - | Roof access with emergency egress | 3pr. hinges; sashlock, single master-keyed security cylinder and turn, 1no. Euro escutcheon, 1no. lever handle on rose; 2no. 90° hold-open restrictors; 2no. flush bolts; 50mm dia. Door ID disc (external lever handle to release lock bolt for emergency egress)
E5c | Aluminium | 1 | Single | - |  | Restrictor | Single lever | Cylinder inside only | N/A | - | N/A | - | - | - | Roof access with emergency egress | 1.5pr. hinges; sashlock for narrow stile, single master-keyed security cylinder and turn, 1no. Euro escutcheon, 1no. lever handle on rose; 90° hold-open restrictor; 50mm dia. Door ID disc (external lever handle to release lock bolt for emergency egress)
E5d | Aluminium | 2 | Single | - |  | 2 Restrictors | Single lever | Cylinder inside only | Flush | - | N/A | - | - | - | Courtyard access with emergency egress | 3pr. hinges; sashlock, single master-keyed security cylinder and turn, 1no. Euro escutcheon, 1no. lever handle on rose; 2no. 90° hold-open restrictors; 2no. flush bolts; 50mm dia. Door ID disc (external lever handle to release lock bolt for emergency egress)
E6a | Steel | 1 | Single | - |  | Restrictor | - | External cylinder | N/A | - | N/A | - | - | - | HV Switchroom | 1.5pr. hinges; push pad emergency exit mortice nightlatch, single master-keyed security cylinder, 1no. Euro cylinder pull; 90° hold-open restrictor; 50mm dia. Door ID disc
E6b | Steel | 2 | Single | - |  | Restrictor | - | External cylinder | Surface | - | N/A | - | - | - | HV Switchroom | 4pr. hinges; push pad emergency exit mortice nightlatch, single master-keyed security cylinder, 1no. Euro cylinder pull; 450mm surface bow handle bolt (bottom); 900mm surface bow handle bolt (top); 2no. 90° hold-open restrictors; 50mm dia. Door ID disc
E7 | Steel | 1 | Single | - |  | - | Single lever | Latch | N/A | - | N/A | - | - | - | Door in screen wall | 2pr. extra heavy duty hinges; mortice latch, 1no. lever handle on rose (for one-sided operation); 90° hold-open restrictor; 50mm dia. Door ID disc
E8 | Steel | 2 | Single | - |  | - | - | 2no. Cylinder inside only | Flush | - | N/A | - | - | - | MRI maintenance access | 4pr. Hinges; 2no. sashlock, single master-keyed security cylinder, Euro escutcheon; 2no. flushbolts; 2no. heavy duty 90° hold-open restrictors; 50mm dia. Door ID disc

## Notes
- P012X-BDP-A-EL-XX-X-21001 – 21018 - P012X-BDP-A-EL-40-X-21001 and 21002 - P012X-BDP-A-EL-XX-X-31001 - P012X-BDP-A-EL-XX-X-31002 - P012X-BDP-A-EL-XX-X-31003
- P012X-AEC-E-GA-XX-0-681 - P012X-AEC-E-GA-XX-1-681 - P012X-AEC-E-GA-XX-2-681 - P012X-AEC-E-GA-XX-3-681